|  | HVAC WORK ORDER Alder Residence — Portland, OR |
| --- | --- |

| Customer | Casey Alder |
| --- | --- |
| Address | 1234 SE Alder St, Portland, OR 97215 |
| Phone | (503) 555-0136 |
| Questions on site | Kyle — (503) 555-0117 |
| Job # | 2026-0714 |
| Install Dates | ___________________________ |
| Crew Lead | ___________________________ |

⚠  SAFETY FLAGS: LEAD PAINT — 1962 home, lead-safe (RRP) practices on any paint disturbance

Scope of Work

| Task | Details | Location |
| --- | --- | --- |
| Remove gas furnace | Cap gas at the appliance, remove furnace + attic duct runs, haul away | Hall closet + attic |
| Install ductless heat pump | 24k cold-climate outdoor unit on east wall pad, 12k wall head (living), 9k wall head (bedroom), linesets through attic | East wall, living room, bedroom |
| Range hood duct | Duct new 300 CFM hood through upper cabinet, out the wall cap with damper | Kitchen |
| Bath fan | ENERGY STAR 110 CFM fan with humidistat, duct out the roof, first 3 ft straight | Hall bath |

Equipment Arriving

| Item | Model | Qty |
| --- | --- | --- |
| Outdoor unit | 24k cold-climate ductless ODU | 1 |
| Wall heads | 12k (living) + 9k (bedroom) | 2 |
| Bath fan | 110 CFM ENERGY STAR, humidistat | 1 |
| Range hood | 300 CFM ducted | 1 |
| Disconnect + whip | 60A non-fused | 1 |

Burch QA — Heat Pump Installation (Ductless)

☐  All indoor heads mounted and connected (Q81)

☐  All zones tested in heat AND cool mode (Q82)

☐  Manufacturer remotes/controls operational for each zone (Q83)

☐  ODU installed on permanent pad, stable, level, secured (Q75-76)

☐  Line set length recorded + insulation covers the full run (Q78, Q80)

☐  Condensate drains sloped and terminated clear of the building (Q79)

Burch QA — Commissioning Diagnostics

| Test | Value | Pass? |
| --- | --- | --- |
| HP Airflow (CFM) | ________ | ☐ |
| CFM/ton (target 350-400) | ________ | ☐ |
| Supply static pressure (in. WG) | ________ | ☐ |
| Return static upstream of filter (in. WG) | ________ | ☐ |
| Return static downstream of filter (in. WG) | ________ | ☐ |
| Pressure pan test — avg < 1.5, no single > 2 (Q60) | ________ | ☐ |
| Room pressurization — no room > 3 Pa (Q62) | ________ | ☐ |

Burch QA — Bath Exhaust Fans

☐  Fan flow: 20+ CFM continuous OR 50+ CFM intermittent (Q88)

☐  ENERGY STAR certified (Q89)

☐  Automated controls — timer or humidistat (Q90)

☐  Duct terminates OUTDOORS — clear of attic, crawl, and floor cavities (Q91)

☐  First 3 feet of duct off the fan run straight (Q92)

☐  Outlet 10+ ft from any air inlet (Q93)

☐  All duct seams sealed mastic/UL-181 (Q94)

☐  Wall cap includes damper (Q95)

Burch QA — Kitchen Exhaust Fan

☐  Minimum 100 CFM measured flow (Q97)

☐  ENERGY STAR certified (Q98)

☐  Vents outdoors on the direct route, no bends first 3 ft (Q99)

☐  Duct seams sealed mastic/UL-181 (Q101)

☐  Wall cap includes damper (Q102)

Permits

☐  Permits closed out for EACH inspected installed measure (Q162)

☐  Permit finals scheduled BEFORE requesting the program QA inspection

☐  Inspection cards / permit numbers photographed for the job file

Burch QA — Homeowner Education (leave-behind)

☐  Occupant informed: run the heat pump as primary — backup ER heat costs more (Q111)

☐  Occupant informed: nighttime setback 4°F or less (Q112)

☐  Occupant informed: use "heat" or "cool", leave "auto" alone (Q113)

☐  Occupant informed: fan speed on "automatic" (Q114)

☐  Occupant informed: filter replacement schedule (Q115)

Notes for Crew

•  Homeowner is on video calls in the back office — knock at the front door, headphones mean go around

•  Keep the driveway clear of material staging after 4pm (street sweeping Tuesday)

•  Cat is friendly and sneaky — check for her before closing the attic hatch

Reference Photos

| Furnace closet, hallway — gas capped at the appliance Day 1 | East wall ODU location — pad here, lineset penetration sealed after ducts run |
| --- | --- |
| Hall bath fan location — duct out the roof, first 3 ft straight | Range wall — hood ducts through the upper cabinet, out the wall cap |

Resilient Retrofits  ·  CCB# 245539  ·  Prepared by: Kyle Kanooth